| SUBJECT* | VANIHCS SPS Water Testing (VA-27-00000760) |
| --- | --- |

GENERAL INFORMATION

| CONTRACTING OFFICE’S ZIP CODE* | 46240-4628 |
| --- | --- |
| SOLICITATION NUMBER* | 36C25027R0012 |
| RESPONSE DATE/TIME/ZONE | 11-04-2026 15:00 EASTERN TIME, NEW YORK, USA |
| ARCHIVE | 15 DAYS AFTER THE RESPONSE DATE |
| SET-ASIDE | SDVOSBC |  |
| PRODUCT SERVICE CODE* | B533 |  |
| NAICS CODE* | 541380 |  |
| PLACE OF PERFORMANCE | VA Northern Indiana Healthcare System (VANIHCS) |  |
|  | Fort Wayne VAMC, 46805 |  |
|  | Marion VAMC, 46953 |  |
|  | Jackie Walorski VA Clinic, Mishawaka, IN 46545 |  |
| POSTAL CODE |  |  |
| COUNTRY |  |  |

CONTACT INFORMATION

| CONTRACTING OFFICE ADDRESS | Department of Veterans Affairs Network Contracting Office 10 8888 Keystone Crossing Suite 325 Indianapolis IN 46240-4628 |
| --- | --- |
| POINT OF CONTACT* | Contract Specialist Eric Sweatt eric.sweatt@va.gov |

ADDITIONAL INFORMATION

| AGENCY’S URL | https://www.va.gov/northern-indiana-health-care |
| --- | --- |
| URL DESCRIPTION | Homepage |
| AGENCY CONTACT’S EMAIL ADDRESS | eric.sweatt@va.gov |
| EMAIL DESCRIPTION | preferred contract |

DESCRIPTION

MODIFICATION STATEMENT OF WORK

Sterile Processing Service ST-108 Testing Requirements Upgrade

The contractor shall provide all the following for testing the water for/within SPS per the ANSI/AAMI ST108:2023 at the Marion, Fort Wayne, and Jackie Walorski VA sites as defined in this Statement of Work (SOW).

- WORK TO BE PERFORMED:

- Contractor shall provide all labor, materials, equipment, transportation, lodging, and supervision necessary to collect appropriate samples and deliver to a lab meeting the requirements for processing of AAMI ST108.

- Contractor shall calibrate the conductivity/resistivity meter monthly during their testing visit and provide a water analysis report.

- The contractor will be part of the multidisciplinary team that assists the water working group with resolving out-of-range water testing, in addition to:

- Serves as the subject matter expert on water testing per the ST108:2023

- Serves as the subject matter expert on corrective actions to mitigate risks for out-of-range water testing parameters.

- Completes monthly, quarterly, and yearly testing per ST108:2023 and the VHA water contract/SOW.

- Completes performance qualification testing per the ST108:2023 and per the VHA contract/SOW.

- The contractor must report any outliers identified during testing within 24 hours of

- receiving laboratory results.

- Completes follow-up testing as ordered by engineering for out-of-range water parameters per the ST108:2023 and VHA water contract/SOW.

- The contractor shall provide VA end users with access to web-based reporting software for ongoing review of water testing data, historical trends, and compliance documentation.

- All reports must clearly highlight or delineate outliers and be designed to provide ease of reading, ensuring information is presented in a clear, organized, and actionable format.

- Contractor shall provide consultative services as needed, such as resolving abnormal water testing results, water system analysis, and mitigation of test results.

AAMI ST108 UTILITY WATER, CRITICAL WATER, AND STEAM TESTING BY VENDOR:

| Fort Wayne – Routine (monthly) POU Testing by Vendor | Fort Wayne – Routine (monthly) POU Testing by Vendor | Fort Wayne – Routine (monthly) POU Testing by Vendor | Fort Wayne – Routine (monthly) POU Testing by Vendor | Fort Wayne – Routine (monthly) POU Testing by Vendor | Fort Wayne – Routine (monthly) POU Testing by Vendor | Fort Wayne – Routine (monthly) POU Testing by Vendor | Fort Wayne – Routine (monthly) POU Testing by Vendor | Fort Wayne – Routine (monthly) POU Testing by Vendor |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Water Quality Measurement | Units | Type of Testing | Routine Sample Site Utility | Routine Sample Site Critical | Minimum Frequency of Testing and Testing Range | Minimum Frequency of Testing and Testing Range | Minimum Frequency of Testing and Testing Range | Minimum Frequency of Testing and Testing Range |
| Water Quality Measurement | Units | Type of Testing | Routine Sample Site Utility | Routine Sample Site Critical | Utility Water | Utility Water | Critical Water | Critical Water |
| pH | pH | pH Meter or Colorimetric dipsticks | Medivator Basin x4 | Decon sinks x3 Washer x1 Ultrasonic x1 Eye Ultrasonic X1 | 6.5-9.5 | Monthly | 5.0-7.5 | Monthly |
| Conductivity | uS/cm | Conductivity Meter | Medivator Basin x4 | Decon sinks x3 Washer x1 Ultrasonic x1 Eye UltrasonicX1 | <500 | Monthly | <10 | Monthly |
| Total Alkalinity | mg CaCO3/L | Colorimetric dipsticks or Alkalinity test kit | Medivator Basin x4 | Decon sinks x3 Washer x1 Ultrasonic x1 Eye Ultrasonic X1 | <400 | Monthly | <8 | Monthly |
| Total Hardness | mg CaCO3/L | Determination of ppm as CaCO3/L by colorimetric dipsticks, titration kit, or handheld meter | Medivator Basin x4 | Decon sinks x3 Washer x1 Ultrasonic x1 Eye Ultrasonic X1 | <150 | Monthly | <1 | Monthly |
| Bacteria | CFU/mL | Heterotrophic Plate Count (HPC) | NA | Decon sinks x3 Medivator Basin x4 Washer x1 Ultrasonic x1 Eye Ultrasonic X1 | <500 | Monthly | <10 | Monthly |
| Endotoxin | EU/mL | LAL Test | NA | Decon sinks x3 Medivator Basin x4 Washer x1 Ultrasonic x1 Eye Ultrasonic X1 | NA | NA | <10 | Monthly |

| Fort Wayne – Point of Generation Routine (monthly) Testing by Vendor | Fort Wayne – Point of Generation Routine (monthly) Testing by Vendor | Fort Wayne – Point of Generation Routine (monthly) Testing by Vendor | Fort Wayne – Point of Generation Routine (monthly) Testing by Vendor | Fort Wayne – Point of Generation Routine (monthly) Testing by Vendor | Fort Wayne – Point of Generation Routine (monthly) Testing by Vendor |
| --- | --- | --- | --- | --- | --- |
| Water Quality Measurement | Units | Type of Testing | Routine Sample Site Critical | Minimum Frequency of Testing and Testing Range | Minimum Frequency of Testing and Testing Range |
| Water Quality Measurement | Units | Type of Testing | Routine Sample Site Critical | Critical Water | Critical Water |
| pH | pH | pH Meter or Colorimetric dipsticks | Loop Supply Loop Return | 5.0-7.5 | Monthly |
| Conductivity | uS/cm | Conductivity Meter (in line or measurement of a collected sample) | Loop Supply Loop Return | <10 | Monthly |
| Total Alkalinity | mg CaCO3/L | Colorimetric dipsticks or Alkalinity test kit | Loop Supply Loop Return | <8 | Monthly |
| Total Hardness | mg CaCO3/L | Determination of ppm as CaCO3/L by colorimetric dipsticks, titration kit, or handheld meter | Loop Supply Loop Return | <1 | Monthly |
| Bacteria | CFU/mL | Heterotrophic Plate Count (HPC) | Loop Supply Loop Return | <10 | Monthly |
| Endotoxin | EU/mL | LAL Test | Loop Supply Loop Return | <10 | Monthly |

| Fort Wayne – Performance Qualification Testing (quarterly) Testing by Vendor | Fort Wayne – Performance Qualification Testing (quarterly) Testing by Vendor | Fort Wayne – Performance Qualification Testing (quarterly) Testing by Vendor | Fort Wayne – Performance Qualification Testing (quarterly) Testing by Vendor | Fort Wayne – Performance Qualification Testing (quarterly) Testing by Vendor | Fort Wayne – Performance Qualification Testing (quarterly) Testing by Vendor | Fort Wayne – Performance Qualification Testing (quarterly) Testing by Vendor | Fort Wayne – Performance Qualification Testing (quarterly) Testing by Vendor | Fort Wayne – Performance Qualification Testing (quarterly) Testing by Vendor | Fort Wayne – Performance Qualification Testing (quarterly) Testing by Vendor | Fort Wayne – Performance Qualification Testing (quarterly) Testing by Vendor | Fort Wayne – Performance Qualification Testing (quarterly) Testing by Vendor |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Water Quality Measurement | Units | Type of Testing | PQ Sample Site Utility | PQ Sample Site Critical | PQ Sample Site Steam | Minimum Frequency of Testing and Testing Range | Minimum Frequency of Testing and Testing Range | Minimum Frequency of Testing and Testing Range | Minimum Frequency of Testing and Testing Range | Minimum Frequency of Testing and Testing Range | Minimum Frequency of Testing and Testing Range |
| Water Quality Measurement | Units | Type of Testing | PQ Sample Site Utility | PQ Sample Site Critical | PQ Sample Site Steam | Utility Water | Utility Water | Critical Water | Critical Water | Steam | Steam |
| pH | pH | pH Meter or Colorimetric dipsticks | Decon sinks x4 Medivator Basin x4 Washer x2 Ultrasonic x2 Eye Ultrasonic X2 City Water Water Softener Utility DI After Carbon Filter Medivator 1 Supply Medivator 2 Supply | Decon sinks x3 Washer x1 Ultrasonic x1 Eye Ultrasonic X1 Loop Supply Loop Return After RO After DI | Sterilizer x2 | 6.5-9.5 | Quarterly | 5.0-7.5 | Monthly | 5.0-9.2 | Quarterly |
| Conductivity | uS/cm | Conductivity Meter | Decon sinks x4 Medivator Basin x4 Washer x2 Ultrasonic x2 Eye Ultrasonic X2 City Water Water Softener Utility DI After Carbon Filter Medivator 1 Supply Medivator 2 Supply | Decon sinks x3 Washer x1 Ultrasonic x1 Eye Ultrasonic X1 Loop Supply Loop Return After RO After DI | Sterilizer x2 | <500 | Quarterly | <10 | Monthly | <10 | Quarterly |
| Total Alkalinity | mg CaCO3/L | Colorimetric dipsticks or Alkalinity test kit | Decon sinks x4 Medivator Basin x4 Washer x2 Ultrasonic x2 Eye Ultrasonic X2 City Water Water Softener Utility DI After Carbon Filter Medivator 1 Supply Medivator 2 Supply | Decon sinks x3 Washer x1 Ultrasonic x1 Eye Ultrasonic X1 Loop Supply Loop Return After RO After DI | Sterilizer x2 | <400 | Quarterly | <8 | Monthly | <8 | Quarterly |
| Total Hardness | mg CaCO3/L | Determination of ppm as CaCO3/L by colorimetric dipsticks, titration kit, or handheld meter | Decon sinks x4 Medivator Basin x4 Washer x2 Ultrasonic x2 Eye Ultrasonic X2 City Water Water Softener Utility DI After Carbon Filter Medivator 1 Supply Medivator 2 Supply | Decon sinks x3 Washer x1 Ultrasonic x1 Eye Ultrasonic X1 Loop Supply Loop Return After RO After DI | Sterilizer x2 | <150 | Quarterly | <1 | Monthly | <1 | Quarterly |
| Total Organic Carbon (TOC) | mg/L (ppm) |  | NA | Decon sinks x3 Washer x1 Ultrasonic x1 Eye Ultrasonic X1 Loop Supply Loop Return After RO After DI | NA | NA | NA | <1.0 | Quarterly | NA | NA |
| Aluminum | mg/L |  | Decon sinks x4 Medivator Basin x4 Washer x2 Ultrasonic x2 Eye Ultrasonic X2 City Water Water Softener Utility DI After Carbon Filter Medivator 1 Supply Medivator 2 Supply | Decon sinks x3 Washer x1 Ultrasonic x1 Eye Ultrasonic X1 Loop Supply Loop Return After RO After DI | Sterilizer x2 | <0.1 | Quarterly | <0.1 | Quarterly | <0.1 | Quarterly |
| Chloride | mg/L |  | Decon sinks x4 Medivator Basin x4 Washer x2 Ultrasonic x2 Eye Ultrasonic X2 City Water Water Softener Utility DI After Carbon Filter Medivator 1 Supply Medivator 2 Supply | Decon sinks x3 Washer x1 Ultrasonic x1 Eye Ultrasonic X1 Loop Supply Loop Return After RO After DI | Sterilizer x2 | <250 | Quarterly | <1 | Quarterly | <1 | Quarterly |
| Copper | mg/L |  | Decon sinks x4 Medivator Basin x4 Washer x2 Ultrasonic x2 Eye Ultrasonic X2 City Water Water Softener Utility DI After Carbon Filter Medivator 1 Supply Medivator 2 Supply | Decon sinks x3 Washer x1 Ultrasonic x1 Eye Ultrasonic X1 Loop Supply Loop Return After RO After DI | Sterilizer x2 | <0.1 | Quarterly | <0.1 | Quarterly | <0.1 | Quarterly |
| Iron | mg/L |  | Decon sinks x4 Medivator Basin x4 Washer x2 Ultrasonic x2 Eye Ultrasonic X2 City Water Water Softener Utility DI After Carbon Filter Medivator 1 Supply Medivator 2 Supply | Decon sinks x3 Washer x1 Ultrasonic x1 Eye Ultrasonic X1 Loop Supply Loop Return After RO After DI | Sterilizer x2 | <0.1 | Quarterly | <0.1 | Quarterly | <0.1 | Quarterly |
| Manganese | mg/L |  | Decon sinks x4 Medivator Basin x4 Washer x2 Ultrasonic x2 Eye Ultrasonic X2 City Water Water Softener Utility DI After Carbon Filter Medivator 1 Supply Medivator 2 Supply | Decon sinks x3 Washer x1 Ultrasonic x1 Eye Ultrasonic X1 Loop Supply Loop Return After RO After DI | Sterilizer x2 | <0.1 | Quarterly | <0.1 | Quarterly | <0.1 | Quarterly |
| Nitrate | mg/L |  | Decon sinks x4 Medivator Basin x4 Washer x2 Ultrasonic x2 Eye Ultrasonic X2 City Water Water Softener Utility DI After Carbon Filter Medivator 1 Supply Medivator 2 Supply | Decon sinks x3 Washer x1 Ultrasonic x1 Eye Ultrasonic X1 Loop Supply Loop Return After RO After DI | Sterilizer x2 | <10 | Quarterly | <1 | Quarterly | <1 | Quarterly |
| Phosphate | mg/L |  | Decon sinks x4 Medivator Basin x4 Washer x2 Ultrasonic x2 Eye Ultrasonic X2 City Water Water Softener Utility DI After Carbon Filter Medivator 1 Supply Medivator 2 Supply | Decon sinks x3 Washer x1 Ultrasonic x1 Eye Ultrasonic X1 Loop Supply Loop Return After RO After DI | Sterilizer x2 | <5 | Quarterly | <1 | Quarterly | <1 | Quarterly |
| Silicate | mg/L |  | Decon sinks x4 Medivator Basin x4 Washer x2 Ultrasonic x2 Eye Ultrasonic X2 City Water Water Softener Utility DI After Carbon Filter Medivator 1 Supply Medivator 2 Supply | Decon sinks x3 Washer x1 Ultrasonic x1 Eye Ultrasonic X1 Loop Supply Loop Return After RO After DI | Sterilizer x2 | <50 | Quarterly | <1 | Quarterly | <1 | Quarterly |
| Sulfate | mg/L |  | Decon sinks x4 Medivator Basin x4 Washer x2 Ultrasonic x2 Eye Ultrasonic X2 City Water Water Softener Utility DI After Carbon Filter Medivator 1 Supply Medivator 2 Supply | Decon sinks x3 Washer x1 Ultrasonic x1 Eye Ultrasonic X1 Loop Supply Loop Return After RO After DI | Sterilizer x2 | <150 | Quarterly | <1 | Quarterly | <1 | Quarterly |
| Zinc | mg/L |  | Decon sinks x4 Medivator Basin x4 Washer x2 Ultrasonic x2 Eye Ultrasonic X2 City Water Water Softener Utility DI After Carbon Filter Medivator 1 Supply Medivator 2 Supply | Decon sinks x3 Washer x1 Ultrasonic x1 Eye Ultrasonic X1 Loop Supply Loop Return After RO After DI | Sterilizer x2 | <0.1 | Quarterly | <0.1 | Quarterly | <0.1 | Quarterly |
| Bacteria | CFU/mL | Heterotrophic Plate Count (HPC) | Decon sinks x4 Washer x2 Ultrasonic x2 Eye Ultrasonic X2 City Water Water Softener Utility DI After Carbon Filter Medivator 1 Supply Medivator 2 Supply | Decon sinks x3 Medivator basin x4 Washer x1 Ultrasonic x1 Eye Ultrasonic X1 Loop Supply Loop Return After RO After DI | NA | <500 | Quarterly | <10 | Monthly | NA | NA |
| Endotoxin | EU/mL | LAL Test | NA | Decon sinks x3 Medivator basin x4 Washer x1 Ultrasonic x1 Eye Ultrasonic X1 Loop Supply Loop Return After RO After DI | NA | NA | NA | <10 | Monthly | NA | NA |

| Marion – Routine (monthly) POU Testing by Vendor | Marion – Routine (monthly) POU Testing by Vendor | Marion – Routine (monthly) POU Testing by Vendor | Marion – Routine (monthly) POU Testing by Vendor | Marion – Routine (monthly) POU Testing by Vendor | Marion – Routine (monthly) POU Testing by Vendor |
| --- | --- | --- | --- | --- | --- |
| Water Quality Measurement | Units | Type of Testing | Routine Sample Site Critical | Minimum Frequency of Testing and Testing Range | Minimum Frequency of Testing and Testing Range |
| Water Quality Measurement | Units | Type of Testing | Routine Sample Site Critical | Critical Water | Critical Water |
| pH | pH | pH Meter or Colorimetric dipsticks | Decon sinks x1 Washer x1 | 5.0-7.5 | Monthly |
| Conductivity | uS/cm | Conductivity Meter | Decon sinks x1 Washer x1 | <10 | Monthly |
| Total Alkalinity | mg CaCO3/L | Colorimetric dipsticks or Alkalinity test kit | Decon sinks x1 Washer x1 | <8 | Monthly |
| Total Hardness | mg CaCO3/L | Determination of ppm as CaCO3/L by colorimetric dipsticks, titration kit, or handheld meter | Decon sinks x1 Washer x1 | <1 | Monthly |
| Bacteria | CFU/mL | Heterotrophic Plate Count (HPC) | Decon sinks x1 Washer x1 | <10 | Monthly |
| Endotoxin | EU/mL | LAL Test | Decon sinks x1 Washer x1 | <10 | Monthly |

| Marion – Point of Generation Routine (monthly) Testing by Vendor | Marion – Point of Generation Routine (monthly) Testing by Vendor | Marion – Point of Generation Routine (monthly) Testing by Vendor | Marion – Point of Generation Routine (monthly) Testing by Vendor | Marion – Point of Generation Routine (monthly) Testing by Vendor | Marion – Point of Generation Routine (monthly) Testing by Vendor |
| --- | --- | --- | --- | --- | --- |
| Water Quality Measurement | Units | Type of Testing | Routine Sample Site Critical | Minimum Frequency of Testing and Testing Range | Minimum Frequency of Testing and Testing Range |
| Water Quality Measurement | Units | Type of Testing | Routine Sample Site Critical | Critical Water | Critical Water |
| pH | pH | pH Meter or Colorimetric dipsticks | Supply | 5.0-7.5 | Monthly |
| Conductivity | uS/cm | Conductivity Meter (in line or measurement of a collected sample) | Supply | <10 | Monthly |
| Total Alkalinity | mg CaCO3/L | Colorimetric dipsticks or Alkalinity test kit | Supply | <8 | Monthly |
| Total Hardness | mg CaCO3/L | Determination of ppm as CaCO3/L by colorimetric dipsticks, titration kit, or handheld meter | Supply | <1 | Monthly |
| Bacteria | CFU/mL | Heterotrophic Plate Count (HPC) | Supply | <10 | Monthly |
| Endotoxin | EU/mL | LAL Test | Supply | <10 | Monthly |

| Marion – Performance Qualification Testing (quarterly) Testing by Vendor | Marion – Performance Qualification Testing (quarterly) Testing by Vendor | Marion – Performance Qualification Testing (quarterly) Testing by Vendor | Marion – Performance Qualification Testing (quarterly) Testing by Vendor | Marion – Performance Qualification Testing (quarterly) Testing by Vendor | Marion – Performance Qualification Testing (quarterly) Testing by Vendor | Marion – Performance Qualification Testing (quarterly) Testing by Vendor | Marion – Performance Qualification Testing (quarterly) Testing by Vendor | Marion – Performance Qualification Testing (quarterly) Testing by Vendor | Marion – Performance Qualification Testing (quarterly) Testing by Vendor | Marion – Performance Qualification Testing (quarterly) Testing by Vendor | Marion – Performance Qualification Testing (quarterly) Testing by Vendor |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Water Quality Measurement | Units | Type of Testing | PQ Sample Site Utility | PQ Sample Site Critical | PQ Sample Site Steam | Minimum Frequency of Testing and Testing Range | Minimum Frequency of Testing and Testing Range | Minimum Frequency of Testing and Testing Range | Minimum Frequency of Testing and Testing Range | Minimum Frequency of Testing and Testing Range | Minimum Frequency of Testing and Testing Range |
| Water Quality Measurement | Units | Type of Testing | PQ Sample Site Utility | PQ Sample Site Critical | PQ Sample Site Steam | Utility Water | Utility Water | Critical Water | Critical Water | Steam | Steam |
| pH | pH | pH Meter or Colorimetric dipsticks | Decon sinks x2 Washer x2 Ultrasonic x2 City Water Water Softener Utility DI After Carbon Filter | Decon sinks x1 Washer x1 Supply After RO After DI | Sterilizer x2 | 6.5-9.5 | Quarterly | 5.0-7.5 | Monthly | 5.0-9.2 | Quarterly |
| Conductivity | uS/cm | Conductivity Meter | Decon sinks x2 Washer x2 Ultrasonic x2 City Water Water Softener Utility DI After Carbon Filter | Decon sinks x1 Washer x1 Supply After RO After DI | Sterilizer x2 | <500 | Quarterly | <10 | Monthly | <10 | Quarterly |
| Total Alkalinity | mg CaCO3/L | Colorimetric dipsticks or Alkalinity test kit | Decon sinks x2 Washer x2 Ultrasonic x2 City Water Water Softener Utility DI After Carbon Filter | Decon sinks x1 Washer x1 Supply After RO After DI | Sterilizer x2 | <400 | Quarterly | <8 | Monthly | <8 | Quarterly |
| Total Hardness | mg CaCO3/L | Determination of ppm as CaCO3/L by colorimetric dipsticks, titration kit, or handheld meter | Decon sinks x2 Washer x2 Ultrasonic x2 City Water Water Softener Utility DI After Carbon Filter | Decon sinks x1 Washer x1 Supply After RO After DI | Sterilizer x2 | <150 | Quarterly | <1 | Monthly | <1 | Quarterly |
| Total Organic Carbon (TOC) | mg/L (ppm) |  | NA | Decon sinks x1 Washer x1 Supply After RO After DI | NA | NA | NA | <1.0 | Quarterly | NA | NA |
| Aluminum | mg/L |  | Decon sinks x2 Washer x2 Ultrasonic x2 City Water Water Softener Utility DI After Carbon Filter | Decon sinks x1 Washer x1 Supply After RO After DI | Sterilizer x2 | <0.1 | Quarterly | <0.1 | Quarterly | <0.1 | Quarterly |
| Chloride | mg/L |  | Decon sinks x2 Washer x2 Ultrasonic x2 City Water Water Softener Utility DI After Carbon Filter | Decon sinks x1 Washer x1 Supply After RO After DI | Sterilizer x2 | <250 | Quarterly | <1 | Quarterly | <1 | Quarterly |
| Copper | mg/L |  | Decon sinks x2 Washer x2 Ultrasonic x2 City Water Water Softener Utility DI After Carbon Filter | Decon sinks x1 Washer x1 Supply After RO After DI | Sterilizer x2 | <0.1 | Quarterly | <0.1 | Quarterly | <0.1 | Quarterly |
| Iron | mg/L |  | Decon sinks x2 Washer x2 Ultrasonic x2 City Water Water Softener Utility DI After Carbon Filter | Decon sinks x1 Washer x1 Supply After RO After DI | Sterilizer x2 | <0.1 | Quarterly | <0.1 | Quarterly | <0.1 | Quarterly |
| Manganese | mg/L |  | Decon sinks x2 Washer x2 Ultrasonic x2 City Water Water Softener Utility DI After Carbon Filter | Decon sinks x1 Washer x1 Supply After RO After DI | Sterilizer x2 | <0.1 | Quarterly | <0.1 | Quarterly | <0.1 | Quarterly |
| Nitrate | mg/L |  | Decon sinks x2 Washer x2 Ultrasonic x2 City Water Water Softener Utility DI After Carbon Filter | Decon sinks x1 Washer x1 Supply After RO After DI | Sterilizer x2 | <10 | Quarterly | <1 | Quarterly | <1 | Quarterly |
| Phosphate | mg/L |  | Decon sinks x2 Washer x2 Ultrasonic x2 City Water Water Softener Utility DI After Carbon Filter | Decon sinks x1 Washer x1 Supply After RO After DI | Sterilizer x2 | <5 | Quarterly | <1 | Quarterly | <1 | Quarterly |
| Silicate | mg/L |  | Decon sinks x2 Washer x2 Ultrasonic x2 City Water Water Softener Utility DI After Carbon Filter | Decon sinks x1 Washer x1 Supply After RO After DI | Sterilizer x2 | <50 | Quarterly | <1 | Quarterly | <1 | Quarterly |
| Sulfate | mg/L |  | Decon sinks x2 Washer x2 Ultrasonic x2 City Water Water Softener Utility DI After Carbon Filter | Decon sinks x1 Washer x1 Supply After RO After DI | Sterilizer x2 | <150 | Quarterly | <1 | Quarterly | <1 | Quarterly |
| Zinc | mg/L |  | Decon sinks x2 Washer x2 Ultrasonic x2 City Water Water Softener Utility DI After Carbon Filter | Decon sinks x1 Washer x1 Supply After RO After DI | Sterilizer x2 | <0.1 | Quarterly | <0.1 | Quarterly | <0.1 | Quarterly |
| Bacteria | CFU/mL | Heterotrophic Plate Count (HPC) | Decon sinks x2 Washer x2 Ultrasonic x2 City Water Water Softener Utility DI After Carbon Filter | Decon sinks x1 Washer x1 Supply After RO After DI | NA | <500 | Quarterly | <10 | Monthly | NA | NA |
| Endotoxin | EU/mL | LAL Test | NA | Decon sinks x1 Washer x1 Supply After RO After DI | NA | NA | NA | <10 | Monthly | NA | NA |

| JWC – Performance Qualification Testing (quarterly) Testing by Vendor | JWC – Performance Qualification Testing (quarterly) Testing by Vendor | JWC – Performance Qualification Testing (quarterly) Testing by Vendor | JWC – Performance Qualification Testing (quarterly) Testing by Vendor | JWC – Performance Qualification Testing (quarterly) Testing by Vendor | JWC – Performance Qualification Testing (quarterly) Testing by Vendor | JWC – Performance Qualification Testing (quarterly) Testing by Vendor | JWC – Performance Qualification Testing (quarterly) Testing by Vendor | JWC – Performance Qualification Testing (quarterly) Testing by Vendor |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Water Quality Measurement | Units | Type of Testing | PQ Sample Site Utility | PQ Sample Site Critical | Minimum Frequency of Testing and Testing Range | Minimum Frequency of Testing and Testing Range | Minimum Frequency of Testing and Testing Range | Minimum Frequency of Testing and Testing Range |
| Water Quality Measurement | Units | Type of Testing | PQ Sample Site Utility | PQ Sample Site Critical | Utility Water | Utility Water | Critical Water | Critical Water |
| pH | pH | pH Meter or Colorimetric dipsticks | Decon sink x2 Medivator Basin x4 Water Softener City Water Medivator 30 Supply Medivator 31 Supply | NA | 6.5-9.5 | Quarterly | 5.0-7.5 | Monthly |
| Conductivity | uS/cm | Conductivity Meter | Decon sink x2 Medivator Basin x4 Water Softener City Water Medivator 30 Supply Medivator 31 Supply | NA | <500 | Quarterly | <10 | Monthly |
| Total Alkalinity | mg CaCO3/L | Colorimetric dipsticks or Alkalinity test kit | Decon sink x2 Medivator Basin x4 Water Softener City Water | NA | <400 | Quarterly | <8 | Monthly |
| Total Hardness | mg CaCO3/L | Determination of ppm as CaCO3/L by colorimetric dipsticks, titration kit, or handheld meter | Decon sink x2 Medivator Basin x4 Water Softener City Water | NA | <150 | Quarterly | <1 | Monthly |
| Total Organic Carbon (TOC) | mg/L (ppm) |  | NA | NA | NA | NA | <1.0 | Quarterly |
| Aluminum | mg/L |  | Decon sink x2 Medivator Basin x4 Water Softener City Water Medivator 30 Supply Medivator 31 Supply | NA | <0.1 | Quarterly | <0.1 | Quarterly |
| Chloride | mg/L |  | Decon sink x2 Medivator Basin x4 Water Softener City Water Medivator 30 Supply Medivator 31 Supply | NA | <250 | Quarterly | <1 | Quarterly |
| Copper | mg/L |  | Decon sink x2 Medivator Basin x4 Water Softener City Water Medivator 30 Supply Medivator 31 Supply | NA | <0.1 | Quarterly | <0.1 | Quarterly |
| Iron | mg/L |  | Decon sink x2 Medivator Basin x4 Water Softener City Water Medivator 30 Supply Medivator 31 Supply | NA | <0.1 | Quarterly | <0.1 | Quarterly |
| Manganese | mg/L |  | Decon sink x2 Medivator Basin x4 Water Softener City Water Medivator 30 Supply Medivator 31 Supply | NA | <0.1 | Quarterly | <0.1 | Quarterly |
| Nitrate | mg/L |  | Decon sink x2 Medivator Basin x4 Water Softener City Water Medivator 30 Supply Medivator 31 Supply | NA | <10 | Quarterly | <1 | Quarterly |
| Phosphate | mg/L |  | Decon sink x2 Medivator Basin x4 Water Softener City Water Medivator 30 Supply Medivator 31 Supply | NA | <5 | Quarterly | <1 | Quarterly |
| Silicate | mg/L |  | Decon sink x2 Medivator Basin x4 Water Softener City Water Medivator 30 Supply Medivator 31 Supply | NA | <50 | Quarterly | <1 | Quarterly |
| Sulfate | mg/L |  | Decon sink x2 Medivator Basin x4 Water Softener City Water Medivator 30 Supply Medivator 31 Supply | NA | <150 | Quarterly | <1 | Quarterly |
| Zinc | mg/L |  | Decon sink x2 Medivator Basin x4 Water Softener City Water Medivator 30 Supply Medivator 31 Supply | NA | <0.1 | Quarterly | <0.1 | Quarterly |
| Bacteria | CFU/mL | Heterotrophic Plate Count (HPC) | Decon sink x2 Water Softener City Water Medivator 30 Supply Medivator 31 Supply | Medivator Basin x4 | <500 | Quarterly | <10 | Monthly |
| Endotoxin | EU/mL | LAL Test | NA | Medivator Basin x4 | NA | NA | <10 | Monthly |

| JWC – Routine (monthly) POU Testing by Vendor | JWC – Routine (monthly) POU Testing by Vendor | JWC – Routine (monthly) POU Testing by Vendor | JWC – Routine (monthly) POU Testing by Vendor | JWC – Routine (monthly) POU Testing by Vendor | JWC – Routine (monthly) POU Testing by Vendor | JWC – Routine (monthly) POU Testing by Vendor | JWC – Routine (monthly) POU Testing by Vendor | JWC – Routine (monthly) POU Testing by Vendor |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Water Quality Measurement | Units | Type of Testing | Routine Sample Site Utility | Routine Sample Site Critical | Minimum Frequency of Testing and Testing Range | Minimum Frequency of Testing and Testing Range | Minimum Frequency of Testing and Testing Range | Minimum Frequency of Testing and Testing Range |
| Water Quality Measurement | Units | Type of Testing | Routine Sample Site Utility | Routine Sample Site Critical | Utility Water | Utility Water | Critical Water | Critical Water |
| pH | pH | pH Meter or Colorimetric dipsticks | Medivator Basin x4 | NA | 6.5-9.5 | Monthly | 5.0-7.5 | Monthly |
| Conductivity | uS/cm | Conductivity Meter | Medivator Basin x4 | NA | <500 | Monthly | <10 | Monthly |
| Total Alkalinity | mg CaCO3/L | Colorimetric dipsticks or Alkalinity test kit | Medivator Basin x4 | NA | <400 | Monthly | <8 | Monthly |
| Total Hardness | mg CaCO3/L | Determination of ppm as CaCO3/L by colorimetric dipsticks, titration kit, or handheld meter | Medivator Basin x4 | NA | <150 | Monthly | <1 | Monthly |
| Bacteria | CFU/mL | Heterotrophic Plate Count (HPC) | NA | Medivator Basin x4 | <500 | Monthly | <10 | Monthly |
| Endotoxin | EU/mL | LAL Test | NA | Medivator Basin x4 | NA | NA | <10 | Monthly |

- SPECIAL WORK REQUIREMENTS:

- Hours of Operation: Onsite testing is to be conducted on the first Federal working day of the month.  Onsite services shall be performed during normal business hours of 8:00 AM to 4:00 PM, Monday – Friday, excluding Federal holidays.  Observed holidays are: New Year’s Day, Martin Luther King Jr. Day, Presidents’ Day, Memorial Day, Independence Day, Labor Day, Columbus Day, Veterans Day, Thanksgiving Day, Christmas Day, and any other day specifically declared a holiday by the President of the United States.