# STATEMENT OF WORK (SOW)

Project Title: HVAC Split System Installation and Interior Restoration

Facility / Location: Seymour Johnson Air Force Base, 1600 Wrights Brothers Ave., Goldsboro, NC 27531 (Room 2821)

## Scope of Work Purpose

The Contractor shall provide all personnel, management, supervision, tools, materials, equipment, transportation, and incidentals necessary to remove, furnish, and install a complete split heat pump system and perform associated interior architectural restoration in Room 2821 at Seymour Johnson Air Force Base.

Purpose

The overall objective of this project is to deliver reliable, efficient climate control to Room 2821 and restore adjacent interior wall surfaces affected during equipment and line set routing.

Detailed Work Breakdown & Technical Requirements

- The Contractor shall lawfully remove and dispose of the existing HVAC unit.

2. HVAC Equipment & Installation The Contractor shall furnish and install:

a. Heat Pump Split System: Approved Make/Model or Equal: American Standard (or approved technical equivalent) Capacity: 2-Ton (24,000 BTU) Efficiency Rating: Minimum 14 SEER Auxiliary Heat: 10 kW Electric Heat Strip

b. Refrigerant Line Set: Supply and install a new, properly sized and insulated copper refrigerant line set connecting the outdoor condensing unit and indoor air handling unit.

c. Controls: Furnish and install one (1) new commercial digital/programmable thermostat. Configure setpoints and verify communication between the thermostat and air handler.

d. Testing, Balancing, and Commissioning: Evacuate, vacuum test, charge, and leak-check the refrigerant lines in accordance with manufacturer specifications. Perform full operational testing of cooling, heating, auxiliary heat (10 kW), defrost cycles, and blower performance.

Interior Repair and Finishing (Sheetrock & Paint)

Following the mechanical installation and lineset routing:

1. Sheetrock Installation / Patching: Repair and install new gypsum wallboard/sheetrock across all wall and ceiling openings created for equipment, ductwork, or refrigerant line penetrations. Tape, mud, and sand all joints and fastener penetrations to achieve a smooth, defect-free, paint-ready surface.

2. Painting & Finishing: Prime all patched and repaired surfaces. Apply finish coat(s) of paint matching the existing surrounding interior wall color and sheen of Room 2821.

Period of Performance & Schedule

1. Working Hours: All work shall be performed during standard base operational hours (typically Monday through Friday, 0730 to 1630 hours), excluding federal holidays, unless prior written authorization is granted by the contracting officer.

2. Access & Security Escort: Base passes, badging, and vehicle registrations for contractor personnel must be cleared through the Visitor Control Center prior to mobilization. All contractor personnel shall comply with installation access control requirements.

3. Project Duration: Work will commence upon receipt of formal Notice to Proceed (NTP) and equipment delivery and must reach final completion within ten (10) business days from start of on-site work unless there is a contracting approved change.

Safety, Environmental, and Site Cleanup

1. Housekeeping: The work area inside Room 2821 and external condenser pad areas must be maintained in a clean, neat, and safe condition daily.

2. Debris Disposal: The Contractor is responsible for the lawful removal and disposal of all construction debris, packaging materials, sheetrock scrap, and unused materials off base premises.

## Warranty, Damages, and Bonding

Workmanship Warranty: The Contractor shall warrant and guarantee all workmanship and installation tasks against defects for a minimum period of one (1) year following final Government acceptance.

Facility Damage Liability: The Contractor bears full financial and operational responsibility for any damage inflicted upon Government facilities, grounds, or utilities resulting from contractor negligence or operations.

In the event of property damage, the Contractor shall immediately provide skilled craftsmen and appropriate materials to restore the damaged property at no cost to the Government.

Bonding Requirement: The Contractor shall provide proof of a performance/surety bond of no less than $10,000.00 USD prior to commencing work.

## Deliverables and Milestone Checklist

| Phase | Deliverable / Milestone | Due / Timeframe |
| --- | --- | --- |
| Pre-Construction | Proof of NC HVAC License, Bond ($10,000), & Personnel Security Roster | Prior to Base Access |
| Mobilization | On-site Walkthrough & Man-Hour Agreement | Within 2 days of Award |
| Execution | Demolition, Equipment Installation, Line Set & Electrical Tie-in | Per agreed schedule |
| Restoration | Drywall Patching, Sheetrock Finishing, & Paint Restoration | Prior to testing |
| Closeout | Functional System Verification & Operational Checkout ( | Prior to final payment |
| Warranty | 1-Year Workmanship Warranty Documentation | Project completion |